## Sheet1
Hastings College - Master Facilities Plan
Building Assessments
|  | Architecture | [6 empty] | Engineering | [6 empty] | Functionality
Building | Average Score | Exterior | Entrances | Interior Finishes | Life Safety | Codes/Accessibility | Superstructure | Conveying Systems | Fire Protection | Plumbing | Mechanical | Power | Lighting | Telecomm | Fire Alarm | Space Size | Technology | Notes
01) Admissions / Daugherty Student Engagement Center | 3.5625 | 4 | 3 | 4 | 3 | 2 | 3 | 2 | 1 | 3 | 3 | 5 | 5 | 5 | 5 | 5 | 4 | Not Sprinkled
02) Hurley-McDonald Hall | 2.25 | 2 | 3 | 2 | 2 | 2 | 3 | 2 | 1 | 2 | 2 | 2 | 3 | 3 | 2 | 2 | 3 | Not Sprinkled
03) Perkins Library | 2.25 | 2 | 3 | 3 | 2 | 2 | 3 | 3 | 1 | 3 | 1 | 2 | 2 | 2 | 2 | 3 | 2 | Not Sprinkled, Unisex restrooms getting updated
04) Kiewit Building | 2.3333 | 3 | 2 | 3 | 2 | 1 | 2 |  | 3 | 3 | 3 | 2 | 3 | 3 | 2 | 1 | 2 | Sprinkled, Had a leak in ceiling around sprinkler head.
05) 706 E. 7th St. Residence | 2.1429 | 2 | 2 | 2 | 2 | 1 | 3 |  | 1 | 2 | 2 | 3 | 3 | 3 | 2 | 2 |  | No Fire Protection, Water Heater 2009
06) 710 E. 7th St. Residence | 2.6429 | 4 | 2 | 2 | 3 | 2 | 3 |  | 1 | 3 | 3 | 3 | 3 | 3 | 3 | 2 |  | Not Sprinkled, 1 WH 2012; 2 WH 2020
07) 714 E. 7th St. Residence | 2.8571 | 4 | 3 | 2 | 3 | 2 | 3 |  | 1 | 3 | 4 | 3 | 3 | 3 | 3 | 3 |  | WH 2012; Furnace 2018
08) Morrison-Reeves Science Center | 4.0625 | 4 | 4 | 4 | 4 | 5 | 5 | 5 | 5 | 3 | 3 | 4 | 3 | 4 | 3 | 5 | 4 | Pressure Issues, nearing life expectancy on systems, need DHW circ pump
09) Calvin H. French Memorial Chapel | 2.1333 | 3 | 3 | 3 | 2 | 1 | 2 |  | 1 | 3 | 1 | 2 | 2 | 3 | 2 | 2 | 2 | New lighting & rigging scheduled, Not Sprinkled, Fire hose, front stage
10) The Stone Health Center | 2.2 | 2 | 2 | 2 | 2 | 2 | 3 |  | 1 | 2 | 1 | 3 | 3 | 4 | 2 | 2 | 2 | Not Sprinkled, HVAC R22 Units
11) Babcock Hall Co-ed Residence | 3.0714 | 3 | 3 | 3 | 3 | 2 | 3 |  | 4 | 2 | 3 | 3 | 3 | 4 | 4 | 3 |  | Some compressor issues, older HW heater
12) Taylor Hall Women’s Residence | 2.0714 | 2 | 2 | 2 | 2 | 2 | 2 |  | 1 | 2 | 1 | 3 | 3 | 4 | 2 | 1 |  | Not Sprinkled
13) Wilson Center | 3.1875 | 2 | 4 | 3 | 4 | 3 | 3 | 2 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | Water issues around perimeter
14) McCormick Hall | 2.125 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 3 | 1 | 2 | 3 | 3 | 2 | 2 | 3 | Not Sprinkled
15) Scott Studio Theatre | 2.2667 | 2 | 3 | 2 | 2 | 2 | 3 |  | 1 | 2 | 1 | 2 | 3 | 3 | 3 | 3 | 2 | Not Sprinkled, improper slope in waste pipe
16) Altman Hall Co-ed First-Year Residence | 2.7143 | 3 | 3 | 2 | 3 | 2 | 3 |  | 3 | 2 | 1 | 2 | 3 | 4 | 4 | 3 |  | Old Boiler, Fan Coils and AHU
17) Batchelder General Services | 2.6 | 2 | 3 | 2 | 2 | 2 | 3 |  | 1 | 3 | 3 | 4 | 3 | 3 | 3 | 3 | 2 | Not Sprinkled
17.1) Batchelder Garage | 3 | 3 | 4 | 3 | 3 | 3 | 4 |  | 1 |  |  | 3 |  |  |  | 3 |  | Not Sprinkled
18) Campus Safety – 846 N. Ash Ave. | 2.1333 | 2 | 2 | 2 | 1 | 1 | 3 |  | 1 | 3 | 2 | 3 | 3 | 4 | 1 | 2 | 2 | No Fire Alarm
19) Bronc Hall Men’s Residence | 3.0714 | 3 | 4 | 3 | 3 | 3 | 3 |  | 3 | 2 | 1 | 4 | 3 | 4 | 4 | 3 |  | Need mixing valve on tank
20) Steinhart Plaza | [17 empty] | Not Reviewed
21) MacKay House (603 E 9th) | 2 | 1 | 1 | 2 | 2 | 1 | 2 |  | 1 | 2 | 2 | 3 | 3 | 3 | 3 | 2 |  | Not Sprinkled, R22, WH 2014
22) Hazelrigg Student Union / Studio 200 | 2.875 | 3 | 4 | 3 | 2 | 3 | 4 | 3 | 1 | 2 | 1 | 3 | 3 | 4 | 2 | 4 | 4 | Under Renovation, Not enough strobes, kitchen is new including HVAC
23) Gray Center | 2.4667 | 3 | 3 | 3 | 2 | 2 | 3 |  | 1 | 3 | 3 | 2 | 3 | 3 | 2 | 2 | 2 | Not Sprinkled, WH 2022
24) Jackson Dinsdale Art Center | 4.6 | 4 | 4 | 5 | 5 | 5 | 5 |  | 5 | 5 | 4 | 5 | 5 | 4 | 5 | 4 | 4 | HVAC has control issues
25) Hayes M. Fuhr Hall of Music | 1.1333 | 1 | 1 | 1 | 1 | 1 | 2 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | Flood Damage
26) The 1882 (new residence hall opening 2026) | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | Under Construction
27) Lynn Farrell Arena/Fleharty Educational Center | 3.75 | 4 | 4 | 5 | 5 | 4 | 4 | 4 | 5 | 3 | 3 | 3 | 3 | 3 | 3 | 4 | 3 | In process of updating units, ERUs need updated
28) Lloyd Wilson Field/Stadium | 3.125 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 2 | 2 | 2 | 3 | 3 | 3 | 3 | 3 | 3 | Water problems, Locker Rooms not sprinkled, No HVAC on 3rd
29) Jack Osborne Track Complex/Garage | 4 | 5 | 5 | 4 | 4 | 4 | 4 |  | 1 |  | 4 | 5 | 4 | 4 |  | 4 |  | Garage and Crows Nest
30) Barrett Alumni Center | 3.2857 | 3 | 4 | 3 | 4 | 4 | 4 |  | 1 | 4 | 3 | 3 | 3 | 3 |  | 4 | 3 | No Fire Alarm, Not Sprinkled
31) Bronco Village Apartments | 3.2143 | 4 | 3 | 3 | 3 | 2 | 4 |  | 3 | 4 | 3 | 3 | 3 | 3 | 3 | 4 |  | Building 917 & 923 not remodeled
32) Physical Fitness Facility | 2.4667 | 4 | 3 | 2 | 3 | 2 | 3 |  | 1 | 3 | 1 | 2 | 3 | 4 | 2 | 2 | 2 | Not Sprinkled, Unit Heaters Damaged, WH 2014
32.1) Physical Fitness Facility Garage | 2.75 | 3 | 3 | 3 | 3 | 3 | 3 |  | 1 | [6 empty] | 3 |  | Not Sprinkled
33) Doris Becker Tennis Facility | [17 empty] | Not Reviewed
34) Sachtleben Observatory | [17 empty] | Not Reviewed
35) Bronco Bikes | 3 | 4 | 4 | 3 | 3 | 3 | 4 |  | 1 | 3 | 3 |  |  |  |  | 2 |  | Bike Repair Shop, Not Sprinkled, Unit Heaters, Compressed Air
36) 607 E 9th St Residence | 2 | 2 | 2 | 2 | 2 | 2 | 2 |  | 1 | 2 | 1 | 3 | 3 |  |  | 2 |  | Rental House
37) 611 E 9th St Residence | 1.75 | 2 | 2 | 2 | 2 | 2 | 1 |  | 1 | 2 | 1 | 2 | 2 |  |  | 2 |  | Rental House
38) 905 N Elm Ave Residence | 2.3333 | 3 | 3 | 2 | 2 | 2 | 3 |  | 1 | 3 | 1 | 3 | 3 |  |  | 2 |  | Rental House
39) 812 N Ash Ave Residence | 2.3333 | 3 | 2 | 2 | 2 | 2 | 3 |  | 1 | 3 | 2 | 3 | 3 |  |  | 2 |  | Rental House
40) 906 E 9th St Residence | 2.25 | 2 | 2 | 3 | 2 | 2 | 2 |  | 1 | 3 | 2 | 3 | 3 |  |  | 2 |  | Rental House
40.1) 906 E 9th St Welding Shop | 2.1818 | 2 | 3 | 2 | 2 | 2 | 2 |  | 1 |  | 2 | 3 | 2 |  |  | 3
41) 919 E 9th St Residence | 2.3333 | 3 | 3 | 2 | 2 | 2 | 3 |  | 1 | 3 | 3 | 2 | 2 |  |  | 2 |  | Rental House
Scoring Criteria
1 = Very poor condition: in need of replacement
2 = Poor condition: nearing end of useful life
3 = Adequate condition: consider long-range upgrades
4 = Good condition: at or near contemporary standards
5 = Excellent condition: recently installed or replaced